## Sheet1
Uputa o načinu popunjavanja: • Ponuditelj je obvezan ispuniti Troškovnik po svim traženim stavkama, na način da popuni stupac "Ponuđene specifikacije" prema opisima u stupcu "Tražene specifikacije" te da upiše proizvođača i model u za to predviđeno mjesto ako je primijenjivo te da popuni polje "Ponuđena dostupnost certifikata". Ponuđena roba mora u cijelosti zadovoljiti minimalne karakteristike koje su opisane u tehničkoj specifikaciji ili biti bolja od opisanih specifikacija. • Ponuditelj ne smije mijenjati navedene tražene tehničke specifikacije • Za sve stavke Troškovnika u kojima se uz navedene tehničke specifikacije traži norma, oznaka ili pak marka, patent, tip ili određeno podrijetlo, ponuditelj može ponuditi „ili jednakovrijedno“. • U stupac "Jedinična cijena bez PDV-a ponuditelj upisuje jedinične cijene u dvije decimale. Ponuditelj upisuje valutu ponude u za to predviđenu ćeliju.
Instructions on filling out the form: • The Bidder is obliged to fill in the Cost Sheet for all required items, by entering the column "Offered specifications" according to descritions from the column "Requested specifications" and by entering the producer and model name if applicable and by entering "Offered available certificate". The offered goods must fully meet the minimum characteristics described in the technical specification or be better than the described specifications. • The bidder may not change the stated required technical specifications • For all items of the Cost Sheet in which, in addition to the stated technical specifications, a standard, marking or trademark, patent, type or certain origin is required, the bidder may bid "or equivalent". • In the column "Unit price excluding VAT", the bidder enters unit prices rounded to two decimal places.The bidder enters the bid currency in the cell provided.
Rashladno postrojenje Chiller plant
Redni broj / No. | Tražene specifikacije / Requested specifications | Ponuđene specifikacije / Offered specifications
1 | Industrijsko rashladno postrojenje voda/glikol Water glycol industrial chiller plant
Naziv proizvođača i modela / Producer and model name
Ukupni kapacitet hlađenja od minimalno 750 kW na -20°C Total cooling capacity of minimum 750 kW at -20°C
Industrijsko rashladno postrojenje se sastoji od: Chiller plant consisting of:
1) Rashladnik/agregat voda/glikol hlađen morskom vodom - kapacitet hlađenja: minimalni pojedinačni kapacitet hlađenja svakog agregata je između 350 - 450 kW na -20°C - hlađenje kondenzatora morskom vodom - shell -tube tip kondenzatora hlađena morskom vodom (CuNiFe ili titanijska cijev kondenzatora) - shell tube isparivača (bakrene cijevi + čelična školjka) za sekundarnu mješavinu glikola i vode na -30°C - vijčani kompresor jednostruki ili dvostruki - temperatura okoline: 10-35°C - kontrola ekspanzije: ekspanzijski ventil - rashladni medij za niske temperature koji isključuje CO2 - uključiti u osnovnu cijenu - napajanje 380 V/ 50 Hz - ulazna/izlazna temperatura glikola: -25/-30 °C - ulazne temperature morske vode: 15°C (zimi) i 25°C (ljeti) 1) Seawater cooled water/glycol chillers - cooling capacity : minimum cooling capacity of each chiller is at range 350 kW up to 450 kW at 20°C - seawater condenser cooling - condenser seawater cooled unit (CuNiFe or titanium condenser shell an tube ) - evaporator shell and tube (copper tubes +steel shell) for secondary glycol-water mixture for -30°C - screw compressor single or dual - ambient temperature: 10-35°C - expansion control: expansion valve - refrigeration media for low temperatures that excludes CO2 - to be included in the basic price - power supply 380 V/ 50 Hz - inlet /outlet glycol temperature: -25/-30 °C - seawater inlet temperatures: 15°C (at winter) and 25°C (at summer)
Rashladnik/agregat voda/glikol hlađen morskom vodom smješten na lučkoj obali Seawater cooled water/glycol chillers to be located on the harbor shore
Količina rashladnih agregata: ovisno o ponuđenim rashladnim kapacitetima rashladnih agregata (minimalni ukupni rashladni kapacitet 750 kW na -20°C ili više) i ulazne temperature morske vode 15°C Quantity: dependable of offered chiller cooling capacities (minimum total cooling capacity 750 kW at -20°C or more) and inlet temperature of sea water 15°C
2) sustavi crpljenja morske vode za hlađenje kondenzatora rashladnih agregata - samousisna predpunjiva centrifugalna pumpa - podizanje /total head minimalno 25 metara - kućište od Duplexa - protok: prema zahtjevima rashladnog agregata - kompletan pumpni set s pumpom, samousisnim/predpunjivim sustavom i kontrolnom pločom na skid platformi 2) seawater pumping systems for chillers condenser cooling - selfprimed centrifugal pump - pumping head lift minimum 25 metars - housing made of Duplex - flow according to chiller requirements - complete pumping set with pump, self priminng system , and control panel on skid platform
Količina sustava crpljenja morske vode za hlađenje kondenzatora rashladnih agregata: ovisno o broju ponuđenih rashladnih uređaja Quantity of seawater pumping systems for chillers condenser cooling: dependable on number of offered chillers
3) Sustav cjevovoda morske vode za kondenzatore rashladnog agregata Sastoji se od: A) SS 316L (ili jednakovrijedan) čelične cijevi s promjerom od minimalno 100 mm, svaka dovodna cijev za morsku vodu rashladnog agregata minimalne duljine od 10 metara, prirubnički priključci Količina: ovisno o broju ponuđenih rashladnih uređaja B) filter/strainer za usisne cijevi morske vode rashladnog agregata, ventili, flanže, temperaturni senzori, senzori pritiska i drugo Količina: ovisno o broju ponuđenih rashladnih uređaja 3) Seawater piping system for chiller condensers Consists of : A) SS 316L (or equivalent) steel pipes with diammetar of minimum 100 mm, each chiller seawater intake pipe minimum length of 10 metars , flange connections Quantity : dependable on number of offered chillers B) filter / strainer for chiller seawater intake piping, valves, flanges, temperature sensors, pressure sensors and others Quantity: dependable on number of offered chillers 3a) Sustav cjevovoda primarnog kiuga ( čiler-spremnik) koji se sastoji od cjevovoda(SS 316 L) odgovarajućeg promjera , pojedinačnih pumpi čilera , ventila, fltera , flanđi , temp senzora , senzora pritiska idruga pripadajuća opreme Količine : sukladno zahtjevima i karakterstikama čiler uređaja 3a)The piping system of the primary circuit (chiller-tank) consisting of :piping (SS 316 L) of the appropriate diameter, individual chiller pumps, valves, filters, flanges, temp sensors, pressure sensors and other related equipment Quantities: according to the requirements and characteristics of the chiller device
4) Spremnik rashladnog medija voda/glikol kapaciteta minimalno 10 m3 sa izolacijom i pripadajućim priključcima 4) Tank for cooled water/glycol with a capacity of at least 2 m3 with insulation and associated connections
Opseg isporuke: - kompletno postrojenje rashladnog sustava s rashladnim agregatima, pumpama i sustavom cjevovoda - potrošni dijelovi za puštanje u rad rashladnog postrojenja - montaža i puštanje u rad postrojenja - CE certifikati opreme, usklađenost s EU direktiva o strojevima i PED direktivama -tehnička dokumentacija rukovanja i održavnja svih uređaja i opreme Scope of delivery: - complete chiller system plant with chillers , pumps and piping system - consumable parts for chiller plant commissioning - instalation and commisioning of plant - CE certificates of equipment, conformity to EU machinery and PED directives - technical documentation of operation and maintenance of all devices and equipment
Brodski rashladni agregati voda/glikol Water/glycol marine chillers
Naziv proizvođača i modela / Producer and model name
Brodski tip rashladnog agregata montiran na skid platformu: 2 komada rashladnih agregata svaki po minimalno 70 kW na -30°C Marine type chiller mounted on skid platform: 2 pieces of cooling aggregates each with a minimum of 70 kW at -30°C
Kapacitet hlađenja: minimalno 140 kW na -30°C Cooling capacity: minimum 140 kW at -30°C
Vijčani kompresor jednostruki sistem Screw compressor single system
Kondenzator hlađen morskom vodom shell - tube tip Condenser cooled by sea water shell - tube type
Temperatura okoline: 10-45°C Ambient temperature: 10-45°C
Kontrola kapaciteta kompresora: VFD inverter Compressor capacity control: VFD inverter
Kontrola ekspanzije: ekspanzijski ventil Expansion control: expansion valve
Rashladni medij za niske temperature koji isključuje CO2 - uključiti u osnovnu cijenu Refrigeration media for low temperatures that excludes CO2 - to be included in the basic price
Napajanje 380 V/ 50 Hz Power supply 380 V/ 50 Hz
Ulazna/izlazna temperatura glikola: -25/- 30°C Inlet /outlet glycol temperature: -25/- 30°C
Ulazne temperature morske vode: 15°C (zimi) i 25°C (ljeti) Seawater inlet temperatures: 15°C (at winter) and 25°C (at summer)
Kučište /shell i cijev isparivača (bakrene cijevi + čelično kučište za sekundarnu mješavinu glikola i vode na -30°C, zaštićeno od korozije Evaporator shell and tube ( copper tubes +steel shell) for secondary glycol-water mixture at -30°C, anticorrosive protected
PLC kontrola agregata sa sustavom zaštite (visoki tlak, niski tlak, tlak ulja, razina ulja, niski tlak vode (protok vode), antifriz, nedostatak faze, prenapon, podnapon, pregrijavanje i preopterećenje) i s upravljačkom pločom PLC chiller control with protection system (high pressure, low pressure, oil pressure, oil level, low water pressure (water flow), anti freeze, lack phase, over voltage, under voltage, overheat and overload) and with control panel
1)Sustav cjevovoda morske vode za kondenzatore rashladnog agregata Sastoji se od: SS 316L (ili jednakovrijedan) čelične cijevi s promjerom od minimalno 50 mm, svaka dovodna cijev za morsku vodu rashladnog agregata minimalne duljine od 45 metara sa opremom: prirubnički priključci, ventili , vibracijki spojevi , Y filteri Količina: ovisno o broju ponuđenih rashladnih uređaja 1) Seawater piping system for chiller condensers Consists of : SS 316L (or equivalent) steel pipes with a minimum diameter of 50 mm, each chiller seawater supply pipe of a minimum length of 45 meters with equipment: flanged connections, valves, vibrating joints, Y filters Quantity : dependable on number of offered chillers 2) Sustav cjevovoda primarnog kruga ( čiler-spremnik) koji se sastoji od cjevovoda(SS 316 L) odgovarajućeg promjera sa toplinskom izolacijom odgovarajuće debljine , pojedinačnih pumpi čilera , ventila, flltera , flanđi ,vibracijskih spojeva temp senzora , senzora pritiska idruga pripadajuća opreme Količine : sukladno zahtjevima i karakterstikama čiler uređaja 2)The piping system of the primary circuit (chiller-tank) consisting of :piping (SS 316 L) of the appropriate diameter related piping thermal insulation ,individual chiller pumps, valves, filters, flanges,vibration joints, temp sensors, pressure sensors and other related equipment Quantities: according to the requirements and characteristics of the chiller device
Spremnik rashladnog medija voda /glikol kapaciteta minimalno 2 m3 sa izolacijom i pripadajučim priključcima Tank for cooled water/glycol with a capacity of at least 2 m3 with insulation and associated connections
Opseg isporuke: -kompletno sastavljen i ožičen uređaj -osnovni potrošni djelovi za potrebe puštanja u rad - montaža i puštanje u rad rashladnog uređaja -tehnička dokumentacija rukovanja i održavnja svih uređaja i opreme -certifikati registara/klase, usklađenost sa direktivama EU Strojna i PED direktiva Scope of delivery: -complete assembled and prewired chiller -instalation and commisioning of chiller - set of consumable parts for chiller commisioning - technical documentation of operation and maintenance of all devices and equipment -ship class certificates, conformity to EU machinery and PED directives
Redni broj / No. | Opis stavke / Item description | Jedinica mjere / Unit | Količina / Quantity | Jedinična cijena bez PDV-a / unit price excluding VAT | Ukupno / Total price excluding VAT
1 | Industrijsko rashladno postrojenje voda/glikol sa brodskim rashladnim agregatima voda/glikol Water glycol industrial chiller plant with water/glycol marine chillers | kompl/set | 1 |  | 0
T | Cijena transporta DDP Brodosplit, PDV neplaćen Transport price DDP Brodosplit, VAT excluded | kompl/set | 1 |  | 0
| Rok isporuke: maksimalno 4 mjeseca od uplate avansa Delivery deadline: maximum 4 months since advance payment |  |  | SVEUKUPNO BEZ PDV-a / TOTAL SUM excluding VAT | 0
| Plaćanje: 50% avansa ukupnog iznosa, 50% nakon testiranja, a prije isporuke Payment: 50% advance of the total amount, 50% after testing and before delivery |  |  | IZNOS PDV-a / VAT ammount
|  |  |  | SVEUKUPNO S PDV-om / TOTAL SUM including VAT | 0
VALUTA PONUDE / BID CURRENCY EUR ili USD / EUR or USD